ATTENTION: Please follow the steps of this procedure precisely, in order to exclude the possibility of damaging the panel.

ATTENTION: ZIP file Password is: upgrade tool first

- Check the current firmware version of your SIMPO panel. You can do that in the system menu 9) Soft. Revision.

- If the version of your panel is lower than 3.6.1 , you need to upload the Upgrade Tool first, before you apply the new firmware version to your Simpo panel. If the panel is not updated with the UPGRADE TOOL first, it will become non-functional and must be returned to Teletek Electronics for service!!!

- If the current version of your panel is 3.6.1 or higher, you may proceed to point 3 of the update procedure. (Upgrade tool is not needed)

- Update your SIMPO panel with the SIMPO UPGRADE TOOL (file №1 in the directory) - *.*bin file, first using the standard update procedure:

2.1 Connect the panel to the computer using USB cable: Normal A to Micro B type.

2.2 Enter access code for level 2 or 3 and choose menu 9) SOFT. REVISION. Wait for the message from Windows Explorer for found new Removable Disk. The panel will display automatically on the screen:

USB Host Detected

1. Copy image file to Removable Disk

2. Make Eject at Removable Disk

> Panel is configured

2.3 Use the Windows Explorer file manager to copy the new image update file (with *.bin extension) in Removable Disk directory. When the copying of the image file completes, remove the Removable Disk, as select Eject option from its dialogue box (right click with the mouse over it).

Note: Do not eject the Removable Disk through the task bar of your PC. It must be ejected with right mouse click on the device in My Computer directory.

2.4 If the data in the image file are correct, the panel starts the firmware update procedure of the main microprocessor accompanied with short beeps.

2.5 Disconnect the USB cable. The panel will reset itself automatically after a successful firmware update.

- Update your SIMPO panel again but this time with the new firmware file 3.6.x or higher (file №2 in the directory) *.*bin using the standard update procedure:

2.1 Connect the panel to the computer using USB cable: Normal A to Micro B type.

2.2 Enter access code for level 2 or 3 and choose menu 9) SOFT. REVISION. Wait for the message from Windows Explorer for found new Removable Disk. The panel will display automatically on the screen:

USB Host Detected

1. Copy image file to Removable Disk

2. Make Eject at Removable Disk

> Panel is configured

2.3 Use the Windows Explorer file manager to copy the new image update file (with *.bin extension) in Removable Disk directory. When the copying of the image file completes, remove the Removable Disk, as select Eject option from its dialogue box (right click with the mouse over it).

Note: Do not eject the Removable Disk through the task bar of your PC. It must be ejected with right mouse click on the device in My Computer directory.

2.4 If the data in the image file are correct, the panel starts the firmware update procedure of the main microprocessor accompanied with short beeps.

2.5 Disconnect the USB cable. The panel will reset itself automatically after a successful firmware update.